## Soupape
X Steam Tables
OpenOffice, IF-97 Steam tables.	Valeurs à renseigner dans les cases vertes					source	http://www2.spiraxsarco.com/resources/steam-engineering-tutorials/safety-valves/safety-valve-sizing.asp
By: Magnus Holmgren

Pression de service nominale	4,50	bar absolu
Properties given pressure and enthalpy				Aide
Pression de pleine ouverture	5,00	bar absolu		Pression	5,00		Tsat	151,84	°C
Temperature	240,0	°C		T	240,000		Psat	33,47	bars abs.
Enthalpy	2940,31	kJ/kg
Entropy	7,23	kJ/kgK
Density	2,15	kg/m3
Specific Volume	0,46	m3/kg
Vapour fraction	1,00

Isobaric heat capacity Cp	2,09	kJ/kg
Isochore heat capacity Cv	1,57	kJ/kg
Speed of sound	550,44	m/s
Viscosité dynamique	0,0000177

k=Cp/Cv	1,33

m	5,20	kg/h
C	2,70	lecture C=f(k)
Kdr	0,5
P0	5,00
Ng	0,46
x	1

A (section minimale)	4,08	mm²
Diamètre minimal	2,3	mm

Nota: la formule ISO n'est valide que si le pourcentage de vapeur sèche est au moins égal à 0,9

					Matériau	Acier DH	Inox 302
					diamètre de fil (mm)	de 0,3 à 12	de 0,15 à 15
					masse volumique (Kg/dm3)	7.85	7.90
					G (N/mm2)	81500	70000
					E (N/mm2)	206000	180000
					Rm = f(d) (N/mm2)	2230 - 355.94 Ln (d)	1919 - 255.86 Ln (d)
					Contrainte de torsion maximale admissible τzul	0.50 Rm	0.48 Rm
					Contrainte de flexion maximale admissible σzul	0.70 Rm	0.70 Rm

## Ressort
Calcul de la charge du ressort			Valeurs à renseigner dans les cases vertes
Pression de service nominale	4,50	bar absolu
Pression de pleine ouverture	5,00	bar absolu

Diamètre effectif subissant la pression	3,00	mm
Section effective subissant la pression	7,1	mm²

Précontrainte à la pression de service	3,2	N
Force à pleine levée	3,5	N
Levée totale souhaitée	1	mm

Calcul du ressort
Diamètre moyen	6,00	mm
G Module d'élasticité transversale	76000	N/mm²
Coefficient de Poisson	0,30
E Module d'élasticité (Young)	197600	N/mm²

d diamètre fil marchand	0,6	mm			Aciers à ressorts écrouis à froid
De diamètre extérieur	6,6	mm			d (mm)	G (Mpa)
Di diamètre intérieur	5,4	mm			D =<0,6	88300
D/d rapport d'enroulement	10,00	voir table			0,6< d =<1,5	83400
Raideur souhaitée	0,35	N/mm			1,5< d =<3	81500
					3< d =<6	78500
					d >6	76000
Angle de pente (5 à 8°)	6	degrés						Matériaux	Module de Young E (GPa)		Coeff de Poisson
tangente Â	0,11							Acier de construction	210			Matériaux	Coef
Sa Ecartement théorique minimal entre deux spires	0,23	mm						Acier à ressorts	220			Acier de construction	0,27 - 0,30
p pas conseillé maximum	3,00	mm						Acier inoxydable 18-10	203			Acier inoxydable	0,30 - 0,31
p Pas	2,0	mm						Bronze (cuivre + 9 à 12 % d'étain)	124			Fontes	0,21 - 0,26
c longueur d'une spire active	6,32	mm						Bronze au béryllium	130			Laiton	0,37
Longueur mini théorique développée du fil	116,9	mm						Cuivre laminé U4 (recuit)	90
								Cuivre laminé U4 (écroui dur)	150
								Duralumin AU4G	75
								Fontes	83 à 170
Nbe de spires actives	17	spires						Hastelloy B2 (Ni + Mo)	217
Longueur à vide	34,9	mm						Hastelloy C 2000 (Ni + Cr + Mo)	206
Longueur à spires jointives	11,4	mm						Inconel X-750 (Ni + Cr + Fe)	212 à 218
R réel	0,34	N/mm						Invar	140
Levée totale réelle	1,1	mm						Laiton (Cu + Zn)	100 à 130
De ressort à bloc (spires jointives)	6,63	mm						Monel 400 (Ni + Cu)	173
Force maxi ressort à bloc (spires jointives)	7,9	N						Nimonic 90 (Ni + Cr + Co)	213 à 240
								Nispan (Ni + Cr + Ti)	165 à 200
Racourcissement de précontrainte (pression de service)	9,5	mm						Phynox (Co + Cr + Ni + Mo)	203

Flambement
Conditions d'extrémité: ressort guidé
L0/D	5,81
E	197600	N/mm²
G	76000	N/mm²
D	6,00	mm
Alfa	0,5	lecture dans table		Condition d'extrémités	Alfa
L0/D critique	5,24			deux surfaces plates parallèle avec guidage	0,5
	!! Risque de flambement			une surface plate l'autre sur rotule	0,71
				deux surfaces sur rotules	1
Calcul du flambement				une extrémité immobilisée l'autre libre	2
Lambda_eff=alfa*L0/D	2,91
C1	0,81
C2	6,87
compression critique y_crit	15,5	mm
force critique de flambement	5,2	N

## Calling functions
X Steam Tables			V2,6	http://www,x-eng,com
Steam tables by Magnus Holmgren according to IAPWS IF-97
The macros are stored inside this workbook. (No extra files are needed. Start from a copy of this workbook. This page can be removed)
For error-reporting, feedback, other units etc. contact:					magnus@x-eng,com
The steam tables are free and provided as is. We take no responsibilities for any errors in the code or damage thereby.
OBS: This workbook uses macros. Set security options in Tools:Macro:Security… to enable macros.							Psat

Temperature
Tsat_p	1	bar			99,61	°C	Saturation temperature
T_ph	1	bar	100	kJ/kg	23,84	°C	Temperture as a function of pressure and enthalpy
T_ps	1	bar	1	kJ/(kg K)	73,71	°C	Temperture as a function of pressure and entropy
T_hs	100	kJ/kg	0,2	kJ/(kg K)	13,85	°C	Temperture as a function of enthalpy and entropy
Pressure
psat_T	100	°C			1,01	bar	Saturation pressure
p_hs	84	kJ/kg	0,3	kJ/(kg K)	2,3	bar	Pressure as a function of h and s,
p_hrho	2000	kJ/kg	5	kg/m3	6,05	bar	Pressure as a function of h and rho (density), Very unaccurate for solid water region since it's almost incompressible!
Enthalpy
hV_p	1	bar			2674,95	kJ/kg	Saturated vapour enthalpy
hL_p	1	bar			417,44	kJ/kg	Saturated liquid enthalpy
hV_T	100	°C			2675,57	kJ/kg	Saturated vapour enthalpy
hL_T	100	°C			419,1	kJ/kg	Saturated liquid enthalpy
h_pT	1	bar	20	°C	84,01	kJ/kg	Entalpy as a function of pressure and temperature,
h_ps	1	bar	1	kJ/(kg K)	308,61	kJ/kg	Entalpy as a function of pressure and entropy,
h_px	1	bar	0,5		1546,19	kJ/kg	Entalpy as a function of pressure and vapour fraction
h_Tx	100	°C	0,5		1547,34	kJ/kg	Entalpy as a function of temperature and vapour fraction
h_prho	1	bar	2	kg/m3	1082,77	kJ/kg	Entalpy as a function of pressure and density, Observe for low temperatures (liquid) this equation has 2 solutions, (Not valid!!)
Specific volume
vV_p	1	bar			1,69	m3/kg	Saturated vapour volume
vL_p	1	bar			001,0E-3	m3/kg	Saturated liquid volume
vV_T	100	°C			1,67	m3/kg	Saturated vapour volume
vL_T	100	°C			0	m3/kg	Saturated liquid volume
v_pT	1	bar	100	°C	1,7	m3/kg	Specific volume as a function of pressure and temperature,
v_ph	1	bar	1000	kJ/kg	0,44	m3/kg	Specific volume as a function of pressure and enthalpy
v_ps	1	bar	5	kJ/(kg K)	1,03	m3/kg	Specific volume as a function of pressure and entropy,
Density
rhoV_p	1	bar			0,59	kg/m3	Saturated vapour density
rhoL_p	1	bar			958,64	kg/m3	Saturated liquid density
rhoV_T	100	°C			0,6	kg/m3	Saturated vapour density
rhoL_T	100	°C			958,35	kg/m3	Saturated liquid density
rho_pT	1	bar	100	°C	0,59	kg/m3	Density as a function of pressure and temperature,
rho_ph	1	bar	1000	kJ/kg	2,28	kg/m3	Density as a function of pressure and enthalpy
rho_ps	1	bar	1	kJ/(kg K)	975,62	kg/m3	Density as a function of pressure and entropy,
Specific entropy
sV_p	0,01	bar			9,16	kJ/(kg K)	Saturated vapour entropy
sL_p	0,01	bar			018,4E-6	kJ/(kg K)	Saturated liquid entropy
sV_T	0	°C			9,16	kJ/(kg K)	Saturated vapour entropy
sL_T	100	°C			1,31	kJ/(kg K)	Saturated liquid entropy
s_pT	1	bar	20	°C	0,3	kJ/(kg K)	Specific entropy as a function of pressure and temperature (Returns saturated vapour entalpy if mixture,)
s_ph	1	bar	84,01	kJ/kg	0,3	kJ/(kg K)	Specific entropy as a function of pressure and enthalpy
Specific internal energy
uV_p	1	bar			2505,55	kJ/kg	Saturated vapour internal energy
uL_p	1	bar			417,33	kJ/kg	Saturated liquid internal energy
uV_T	100	°C			2506,02	kJ/kg	Saturated vapour internal energy
uL_T	100	°C			418,99	kJ/kg	Saturated liquid internal energy
u_pT	1	bar	100	°C	2506,17	kJ/kg	Specific internal energy as a function of pressure and temperature,
u_ph	1	bar	1000	kJ/kg	956,21	kJ/kg	Specific internal energy as a function of pressure and enthalpy
u_ps	1	bar	1	kJ/(kg K)	308,51	kJ/kg	Specific internal energy as a function of pressure and entropy,
Specific isobaric heat capacity
CpV_p	1	bar			2,08	kJ/(kg°C)	Saturated vapour heat capacity
CpL_p	1	bar			4,22	kJ/(kg°C)	Saturated liquid heat capacity
CpV_T	100	°C			2,08	kJ/(kg°C)	Saturated vapour heat capacity
CpL_T	100	°C			4,22	kJ/(kg°C)	Saturated liquid heat capacity
Cp_pT	1	bar	100	°C	2,07	kJ/(kg°C)	Specific isobaric heat capacity as a function of pressure and temperature,
Cp_ph	1	bar	200	kJ/kg	4,18	kJ/(kg°C)	Specific isobaric heat capacity as a function of pressure and enthalpy
Cp_ps	1	bar	1	kJ/(kg K)	4,19	kJ/(kg°C)	Specific isobaric heat capacity as a function of pressure and entropy,
Specific isochoric heat capacity
CvV_p	1	bar			1,55	kJ/(kg°C)	Saturated vapour isochoric heat capacity
CvL_p	1	bar			3,77	kJ/(kg°C)	Saturated liquid isochoric heat capacity
CvV_T	100	°C			1,55	kJ/(kg°C)	Saturated vapour isochoric heat capacity
CvL_T	100	°C			3,77	kJ/(kg°C)	Saturated liquid isochoric heat capacity
Cv_pT	1	bar	100	°C	1,55	kJ/(kg°C)	Specific isochoric heat capacity as a function of pressure and temperature,
Cv_ph	1	bar	200	kJ/kg	4,04	kJ/(kg°C)	Specific isochoric heat capacity as a function of pressure and enthalpy
Cv_ps	1	bar	1	kJ/(kg K)	3,9	kJ/(kg°C)	Specific isochoric heat capacity as a function of pressure and entropy,
Speed of sound
wV_p	1	bar			472,05	m/s	Saturated vapour speed of sound
wL_p	1	bar			1545,45	m/s	Saturated liquid speed of sound
wV_T	100	°C			472,26	m/s	Saturated vapour speed of sound
wL_T	100	°C			1545,09	m/s	Saturated liquid speed of sound
w_pT	1	bar	100	°C	472,34	m/s	Speed of sound as a function of pressure and temperature,
w_ph	1	bar	200	kJ/kg	1542,68	m/s	Speed of sound as a function of pressure and enthalpy
w_ps	1	bar	1	kJ/(kg K)	1557,86	m/s	Speed of sound as a function of pressure and entropy,
Dynamic Viscosity
Viscosity is not part of IAPWS Steam IF97. Equations from "Revised Release on the IAPWS Formulation 1985 for the Viscosity of Ordinary Water Substance", 2003 are used.
Viscosity in the mixed region (4) is interpolated according to the density. This is not true since it will be two fases.
my_pT	1	bar	100	°C	0	Pa s	Viscosity as a function of pressure and temperature,
my_ph	1	bar	100	kJ/kg	9,1400E-04	Pa s	Viscosity as a function of pressure and enthalpy
my_ps	1	bar	1	kJ/(kg K)	3,8422E-04	Pa s	Viscosity as a function of pressure and entropy,
Prandtl
Calcualted as Cp*my/tc
pr_pT	1	bar	200	°C	9,5781E-01	-
pr_ph	1	bar	2875,48	kJ/kg	9,5781E-01	-
Thermal Conductivity
Revised release on the IAPS Formulation 1985 for the Thermal Conductivity of ordinary water substance (IAPWS 1998)
tcL_p	1	bar			0,68	W/(m K)	Saturated vapour thermal conductivity
tcV_p	1	bar			0,02	W/(m K)	Saturated liquid thermal conductivity
tcL_T	25	°C			0,61	W/(m K)	Saturated vapour thermal conductivity
tcV_T	25	°C			0,02	W/(m K)	Saturated liquid thermal conductivity
tc_pT	100	bar	350	°C	6,8545E-02	W/(m K)	Thermal conductivity as a function of pressure and temperature,
tc_ph	1	bar	100	kJ/(kg K)	0,61	W/(m K)	Thermal conductivity as a function of pressure and enthalpy
tc_hs	100	kJ/(kg K)	0,34	kJ/(kg K)	0,61	W/(m K)	Thermal conductivity as a function of enthalpy and entropy
Surface Tension
IAPWS Release on Surface Tension of Ordinary Water Substance, September 1994
st_T	100	°C			0,08	N/m	Surface tension for two phase water/steam as a function of T
st_p	1	bar			0,06	N/m	Surface tension for two phase water/steam as a function of T
Vapour fraction
x_ph	1	bar	1000	kJ/kg	0,26		Vapour fraction as a function of pressure and enthalpy
x_ps	1	bar	4	kJ/(kg K)	0,45		Vapour fraction as a function of pressure and entropy,
Vapour Volume Fraction
Observe that vapour volume fraction is very sensitive. Vapour volume is about 1000 times greater than liquid volume and therfore vapour volume fraction
gets close to the accurancy of steam IF-97
vx_ph	1	bar	418	kJ/kg	0,2885		Vapour volume fraction as a function of pressure and enthalpy
vx_ps	1	bar	4	kJ/(kg K)	0,9992		Vapour volume fraction as a function of pressure and entropy,

Version history
News in V2.6
* Error in valid region for function tc_ptrho
* Error in function h3_pt for temperatures near the saturation point.
News in V2.5
* DLL distrubution for use in other applications
* Freebasic translation
* Fixed small error in Cv Region 5 p>1000bar
News in V2.4a
Fixed unit conversion in T_ps region4 (No effekt for SI units.)
News in V2.4
* TODO!!! Check Cv in region 5
* ToDO!!! Tc och my not def. In region 4
* OpenOffice version introduced. (Fixed calculation differences in open office and excel)
* Matlab error giving varaible undefined in some backwards solutions fixed.
News in V2.3
* Option Explicit, gives more efficient calculations.
* Extensive testing
* my_ph not defined in region 4.
* Problems at region border for h4V_p to adress solver problems at the exact border.
* Problem at fast border check in region_ph fixed.
News in V2.2
* Extensive testing
* Fixed error in Cp_ph
* Function p_hrho added. (Very good for calcualting pressure when heating a volume with water/steam mixture.)
* Fixed error in T_hs return no value for vet region bellow the water saturation line.
* Prandtl number added
News in V2.1
* Calling function h_prho
* Fixed problem with Cv reporting NaN in region 5.
* Equivivalent to the Matlab version. (Downloadable from www.x-eng.com)
News in V2
* Calling functions of h and s added.
* Thermal conductivity, Surface tension added
* Calling functions h_px and h_tx added.
* Cp, Cv and w undefined in the mixed region. (Before interpolation with the vapor fraction was used.)
* A work sheet "Properties" for simple lookups added.